|  | Name (Print) | Signature | Date |
| --- | --- | --- | --- |
| Prepared by: |  |  | 10-25-06 |
| Approved by: |  |  |  |
| Approved by: |  |  |  |
| Approved by: |  |  |  |
| Approved by: |  |  |  |
| Approved by: |  |  |  |
| Approved by: |  |  |  |

table of contents

1.0	Introduction	...................................................................................	  3

2.0	Reference Source	........................................................................	  3

3.0	Compliance …………......................................................................	  3

4.0	Definitions………….........................................................................	  4

5.0	Authorized Lockout/Devices.............................................................	  7

6.0	Tags……………….………................................................................	  8

7.0 	Individual Lockout………………………………………………………	  9

8.0	Work Team or Multiple Devices…………………………………..…..      11

9.0	Lock/Tag Removal by A Person Other Than the Person Hanging It	  13

10.0 	Periodic Inspections/Reviews....................................................…...	  14

11.0	Training and Record Keeping ………………………………..………..	  14

12.0	Procurement/Replacements	....................................................	  15

13.0	Responsibility/Accountability.............................................................	  15

1.0	Introduction

1.1	This procedure establishes an energy control standard for the use on XXX Operations equipment and electrical/mechanical power systems. It was developed to provide uniform lockout/tagout try out procedures for all energy sources at XXX:

1.2	To ensure the utmost safety and personnel protection of employees working 	with and maintaining mechanical/electrical equipment; chemicals, fluids, high 	temperatures, gases and stored energy.

1.3	To meet XXX’s HSEC (Health, Safety, Environmental, Community)Fatal Risk 	Control Protocol #8 Isolation, and governmental requirements, to ensure all 	energy hazards are recognized, locked out and tested, to insure total 	isolation of all energy sources, to prevent unexpected startup or release of 	stored energy.

1.4   	HSEC FRCP #8 Isolation applies to all XXX employees, contractors and 	subcontractors working on XXX property or any one who may be exposed to 	equipment or unexpected energized equipment while on property.

2.0	Reference Source

- Federal (MSHA) Standards and Inspections

- State Standards and Inspections

- OSHA Standards

- XXX FRCP #8 Isolation

3.0	Compliance

3.1	All XXX Operations personnel and contractors shall use this procedure.

3.2 	Specific lock-out procedures are reviewed with each employee prior to 	receiving personal locks. Employees shall be trained in the procedure and 	follow it whenever working on XXX Property.

3.3	Contractors working at XXX Operations shall demonstrate they meet the FRCP # 8 Isolation requirements and the requirements of MSHA30 CFR, subchapter 4, part 48.  Furthermore, all contractors are required to be familiar with and adhere to MSHA Standards 57.14105, 56.12016 and 56.12017.

3.4	Contractors who do not meet these requirements shall be trained as required 	by this standard and be required to meet all conditions of this standard.

3.5 	Non-compliance with the lockout procedures is very serious with life and job 		threatening consequences.  Any XXX or Contract personnel who violate the 		established procedures shall be disciplined up to and including discharge.

4.0	Definitions

Affected employee - An employee whose job requires him to operate or use a piece of equipment on which servicing or maintenance is being performed under a lockout, or an employee whose job requires them to be in an area in which such servicing is being performed.

Authorized employee – A person who has been trained in this procedure and Safe Work Procedure (SWP), and who locks out and tags out equipment in order to perform servicing or repairs on equipment, machinery, or other energy sources.

Certified Employee - A person who has been trained to open and close isolation devices, including this procedure and Safe Work Procedure (SWP).  The training will include electrical isolation up to 480 Volts.  Isolation of higher voltages may only be done by those specifically trained for the higher voltages with the proper PPE.

Capable of being locked out - An energy isolating device is capable of being locked out if it has a hasp or other means of attachment to which, or through which, a lock can be affixed, or it has a locking mechanism built into it.

Contractor - A person or persons under the governance of XXX HSEC policies and standard who is temporarily or permanently employed to perform a particular scope of work.

Control device - Push buttons, selector switches, and other circuit control devices used to perform the normal operational startup/shut down of equipment.

Energized - Connected to an energy source or containing residual or stored energy.

Energy Isolating Device - A mechanical device that physically prevents the transmission or release of energy, including but not limited to the following:

- A manually operated circuit breaker.

- A disconnect switch.

- A manually operated switch by which the conductors of a circuit can be disconnected from all ungrounded supply conductors and, in addition, no pole can be operated independently.

- A line valve.

- A block.

- Any similar device.

NOTE:	Push buttons, selector switches, and other control circuit type devices are not energy isolating devices.

Energy Source - Any source of electrical, mechanical, hydraulic, pneumatic, chemical, thermal, or other energy.

Job Procedure/ SWP - A written procedure identifying the job to be performed and the steps necessary to perform it.  It shall include the energy control procedures.

Lead Authorized Person - The maintenance or operations person in charge of the work being performed by a group of personnel.

Lockout - The placement of a lockout device on an energy isolating device, in accordance with an established procedure, ensures that the energy isolating device and the equipment being controlled cannot be operated until the lockout device has been removed.

Lockout device - A device that utilizes a positive physical means to hold an energy isolating device in the safe position.  It prevents the energizing of the equipment, and cannot be easily removed unintentionally.  Included are locks, chains, blind flanges and bolted slip blinds.  A “gang lockout” device is a positive lockout device that enables multiple locks to be placed on a single power isolation switch or valve.

Lock box- is a lockable box which will hold all isolation device lockout keys. They are cable of being locked by multiple lockout devices And constructed in a manner that allows the stamped numbers on the keys to be clearly visible while locked.

Maintenance Work - Workplace activities such as construction, installing, setting up, adjusting, inspecting, modifying, and maintaining/servicing equipment. These activities include lubrication, cleaning or un-jamming, and making adjustments or tool changes, where the employee may be exposed to the unexpected energizing or startup of the equipment or the release of hazardous energy.

Normal Production Operations - The utilization of equipment to perform its intended production function.

Project – A temporary endeavor undertaken to create a unique product or service.

Project Manager- The individual responsible for the managing a project.

Project Team - The members of a project team who are directly involved in the project management activities.

Qualified Authority - A supervisory person knowledgeable in the process and hazards involved.

Setting Up - Any work performed to prepare equipment to perform its normal production operation.

Tag - A prominent warning device and a means of attachment, which can be securely fastened to an energy isolating device in accordance with an established procedure, to indicate that the energy isolating device and the equipment being controlled may not be operated until the tag is removed.  A lockout (red) tag shall always require a lockout device.

Tryout - The physical operation of all control devices after the lockout/tagout has been performed, to ensure that all energy sources have been isolated and stored energy released (where appropriate).  In electrical circuits, it shall include checking each phase to ground and each phase to phase.

5.0	Authorized Lockout Devices

5.1	The safety department maintains a supply of locks sufficient to issue locks to 		all new employees and any current employees needing additional locks. 			Employees requiring new locks must turn in their old lock(s) and key and will 		be issued a new set from stock. The safety department will issue locks, keys,		and personal Danger Tags for lockout. Employees are issued as many as 			necessary based on their jobs requirements.

5.2 	The safety department shall maintain a log sheet of authorized trained 			personnel along with information of when locks were issued and to whom.

5.3	A LOCKOUT PADLOCK SHALL NOT BE USED FOR ANY OTHER 			PURPOSE.

5.4	Any company issued non-series padlock is authorized for use.  A padlock 	which is used for equipment lockout shall be red in color and the core stamped with an exclusive number matching the stamped number on its key.  A red padlock shall	not be used for any other purpose.

5.5  	Departmental or shop locks shall be yellow in color and used as described in this procedure.  A log of all installed department or shop locks will be maintained  and are to include the location of the lock, the reason for the lock, the person placing the lock and the person or persons authorized to remove the lock.

5.6	Locks shall be durable and able to withstand the environment to which they 	are exposed to.

5.7 	An authorized HSEC professional must approve lockout devices.

5.8	Specialized breaker and plug lockouts are authorized for use.  The devices 	shall be capable of being locked by a padlock and shall be red in color.  These 	devices shall be used for no other purpose.

5.9	Chains, slings and cables are authorized for securing valve hand wheels and other special 	purposes. A chain shall be fastened in such a manner so the energy control device it is securing can not be operated.  A “red lockout” lock shall be used to secure the chain, sling or cable.

5.10 	Specialized ball valve/gate valve lockout devices are authorized.  The devices 	shall be capable of being locked by a padlock and shall be red in color.  The 	devices shall be used for no other purpose.

5.11	Blind flanges and bolted slip blinds are authorized for use.  The devices shall 		be capable of being locked by a lockout padlock and shall be red in color.  			The devices shall be used for no other purpose.

5.12	When a machine, equipment, or process must be isolated and locked out for a 		long period of time, periodic inspections should be performed to verify that 		locks/tags are still in place. The frequency of these inspections will vary 			dependent upon the circumstances e.g. active operations vs inactive 			operations.

5.13	There are two methods of energy isolation, individual lockout and group lockout. 		The method to be used in each situation will depend on:

- The complexity of the system

- The number of persons who will place locks

- The number locks to be placed to effectively lock out machine, equipment, or process

The supervisor shall determine which is method is appropriate for each situation and will identify the procedures and method of energy control

6.0 Tags

NOTE: Tagout tags are required to be used with all lockouts.  They are not to 	  be used as a stand-alone lockout device.

6.1	Personal Danger Tag - The Danger tag shall be constructed of a plastic 	material and shall be red, black, and white in color, with a size of 	approximately 6” x 3-1/2”.  A suitably reinforced hole shall be in the tag to 	allow 	for an attachment device.  The tag shall state in bold letters DANGER Do Not 	Operate. Spaces shall be provided for the employee’s name, photo, 	department, date and the reason for equipment locked out.

NOTE: 	No one, under any conditions, shall operate an energy isolation 		device which has a Personal Danger tag attached to it. A Personal 		Danger Tag may be removed only by the individual whose name is 		on the tag or by the appropriate authorized person, supervisor, 		or Manager after following the proper procedures (see 10.0 below)

6.2 	Department/Shop Danger Tag - The Danger tag shall be similar to the Personal Danger tag in construction.  It shall be red, black and white in color with a size of approximately 6” x 3-1/2”. A suitably reinforced hole shall be in the tag to allow for an attachment device. The tag states in bold letters DANGER. Do Not Operate. Spaces are provides for the department and names. A department tag may be placed on any machine or equipment to keep the equipment from being energized. 	A department/shop tag can be removed only by an authorized person from that department or shop.

NOTE:	No one, under any conditions, shall work under or operate an 			energy isolation device which has only a Department /Shop danger 		tag attached to it.

6.3 	The construction, markings, and written information on the tag shall be such 		that deterioration will not occur when exposed to weather and or corrosive 			environments

7.0	Individual Lockout

NOTE:	Every individual working on locked out equipment must place a 		personal lock and tag on lockout device that isolates the power 		from that equipment.  Each employee must install and remove their 		lock and tag..

7.1 	Employee’s working on equipment, that if energized or operated would present a safety hazard to themselves or others shall effectively LOCK OUT and TRY OUT the equipment. Whenever a Personal safety lock is used, a Personal Danger Tag with his/her photo must accompany it. Work may not commence on any electrical or mechanical system unless the appropriate electrical control box is completely and safely LOCKED OUT and TRIED OUT. The employees working on the electrical or mechanical system shall have personal locks and tags in place.

7.2	No one shall work under just a department lock or tag. In the event an 	employee MUST work on a piece of equipment at the same time an 	electrician MUST work on the switchgear supplying that equipment energy, a 	procedure must be 	developed to allow all employees the ability to personally 	Lockout/Tagout and Tryout .

7.3	An authorized employee shall inform the Operations person “owning” or in charge of the	equipment of the need to lockout/tagout the affected equipment.  The Operations person will determine necessary plant conditions and when ready, position the isolation devices for lockout.  In the event that an Operations person is not available, the Operations person “owning” the affected equipment may authorize a qualified employee to position the isolation devices for lockout.

7.4	The authorized employee locking out the equipment shall obtain the appropriate 		job procedure (SWP), or qualified instructions to safely isolate the equipment.  		The equipment shall be shut down following the steps in the 	procedure, using 		assistance as necessary.

7.5	When the equipment is de-energized, the energy isolation device(s) shall be positioned as required, and in the order specified, by the job procedure (SWP).  As each energy isolation device is de-energized, a gang lockout device shall be attached to the isolation device.  The gang lockout device must be attached in such a manner that prevents re-energizing the equipment until the lockout device is removed.  At the same time, a Danger tag shall be attached to the energy isolating device by placing the hasp of the lockout device through the hole in the tag.  The Danger tag shall have the authorized employee’s name and department. Each employee working on the equipment must attach his/her lockout device.

NOTE: 	The opening and closing of any isolation devices on equipment that operates above 480 volts must be done by a trained and certified person. The opening and closing of any isolation devices on equipment that operates at 480 Volts or less must be done by a trained and authorized person.

For all electrical work Ref. Fatal Risk Control Protocol #8 			Appendixes E for proper PPE use.

7.6	When all energy isolation device(s) have been positioned and locked/tagged, all 	equipment control device(s) shall be tested in each mode of operation to ensure 	that no unexpected energy source is available.  When electrical circuits are to 	be worked on, a certified person trained and authorized in the use of electrical test equipment and who normally works with the energy levels involved, shall verify 	using the appropriate test device that no hazardous electrical energy  	sources are contained in the equipment being maintained. After testing, the 	control device(s) shall then be placed in the off (or other wording which means 	the same) position.

Only a trained authorized electrician or instrument technition can work with voltage above 50 Volts, and must have the proper PPE, clothing, equipment and tools to do so.

NOTE:	Electrical verification is not required for portable cord and plug equipment where disconnecting the plug from the receptacle removes all sources of electrical power but still must lock out.

7.7	Any employee who was not present for the initial lockout and tryout and is required to lock out the equipment must ensure that all employees are removed from the equipment and that if the equipment is in such a state, that if it were energized, would not pose a safety hazard or cause undue equipment damage.  The employee shall then proceed with a tryout .

7.8	Upon completion of work, the group responsible for the equipment shall be 		notified.  The authorized employee who locked out the equipment shall inspect 		the equipment to ensure it is ready to return to operation and then shall 			remove his lockout devices.  No control devices shall be repositioned to 		the “on” position while lockout devices are being removed.  If the 			employee who installed the lockout is not available, the lockout shall be 			removed as per Section 9. After insuring all employees, tools, and material 		are clear the responsible person will return control of the equipment to the 			area operator. When multiple crafts are working on a piece of equipment, a 		representative of each craft must notify the operator that their part of the job is 		complete and their locks are being removed.

7.9	If the machinery or equipment unsafe to energize or return to normal service. The authorized employee or employees must install a department shop lock and tag, and then remove their personal safety lock and tag.

7.10	Once all lockout devices have been removed, the equipment shall be made 		ready for operation, using assistance as required.

8.0 	Work Team or Multiple Devices

When multiple employees from the same work team and shift are working on one piece of equipment, or multiple energy isolation devices are involved, the following procedure may be used.

8.1	All Work Team members on the job shall perform the lockout as required by this procedure.  When all energy isolation devices are locked, and the equipment controls have been tested, all keys used for the isolation device lockouts shall be placed in a “lock box” in such a manner that the stamped key numbers are clearly visible without unlocking the box.

8.2	The lead authorized employee shall attach a lockout device to the “lock box”.  	then place his personal lock and tag on the lockout device and it shall be positioned to prevent the “lock box” from being opened.  A lockout tag shall be attached to the lockout device.

8.3	All work team members who are to work on the equipment shall then attach their own lock and tag to the “lock box”.

8.4	Any employee who was not present for the initial lockout and tryout and is required to lock out the equipment must verify the lockout on the lock box by matching the stamped key numbers from the lockbox to the matching stamped lock cores on the isolation devices.  The lead authorized person will then ensure that all employees are removed from the equipment and that if  the equipment were energized it would not pose a safety hazard or cause undue equipment damage.  The lead authorized person will then allow the employee to proceed with a tryout .

8.4	As each work team member completes work, he shall remove his lockout 	device from the “lock box”.  The lead authorized employee(s) May remove his personal lock and tag only to transfer control of the lock box over to another lead authorized employee.. The authorized lead employee(s) will keep their lockout device in place until all other lockout devices are removed from the “lock box”.

NOTE: The authorized employee, upon removing his lockout device from the “lock box”, will take custody of all keys in the “lock box”. He shall inform operations that work is complete and remove the lockout devices from the energy isolating devices

8.5	The work team member applying his lock to the final locked position of the 	multiple lockout device or gang lockouts shall instead obtain a second gang        	lockout device and attach it to the final position. This work team member shall 	then place his lockout lock in the first position of the second gang lockout.  	This ensures other employees the ability to continue to add their locks for 	locking out this equipment.  Lockout removal remains the same as for 	individual lockouts.

9.0	Lock/Tag Removal by a Person Other Than the Person Hanging It

When it is required that a personal lockout lock/tag be removed by someone other than the person who originally installed it, the following steps are required:

9.1	It must be verified that the employee who installed the lockout/tagout device is 	no longer on the facilities or premises.

9.2	All reasonable attempts must be made to contact the employee (personally or 	by telephone) to inform him/her that the device needs to be removed and to 	confirm the employee’s location. The employee (if contacted) may be 	requested to return to the site to remove the lockout. If unable to contact the employee, or the employee is unable to return to the facility, the following steps shall be performed:

9.3	A complete inspection of the affected area must be performed by a	supervisor to ensure that all personnel involved in the lock out are clear and the equipment is safe to return to operating status, before the device is removed.

9.4	A supervisor on shift will accompany the maintenance supervisor or his appointee to the location of the designated lock/tag removal. The shift supervisor shall then personally remove the lockout devices returning the equipment to service as per the appropriate job procedure (SWP).  Documentation of all pervious steps of the lockout device removal shall be documented by the supervisor.

9.5 	Lockout/Tagout Devices Removal form must be completed by the supervisor and distributed as per instructions on the Lockout/Tagout Device Removal form.  Steps taken to contact the employee shall be included on the form. A copy of the form shall be given to the employee’s direct supervisor for inclusion in the employee’s 	personnel file.  Prior to allowing the employee to return to work, the direct supervisor shall inform the employee of the removal of his lockout devices. (Per MSHA Standards 56.12017 and 56.12016 requirements)

10.0	Periodic Inspections/Reviews

10.1	This procedure shall be reviewed annually by safety department personnel 	familiar with HSEC FRCP’S and MSHA to determine if changes are required 	due to changes in HSEC FRCP or governmental regulations. The review shall 	determine that the steps taken for individual pieces of equipment provide the 	maximum protection and the equipment is in good working condition.

10.2	Inspections shall be conducted to verify that the site’s lockout and tagout 	program is effective. This shall include an evaluation of employee’s 	compliance 	with the lockout and tagout program.

10.3	Energy control procedures shall be reviewed as determined by the (SWP and 	Planned/unplanned Observations).  The review shall determine that the steps 	taken for individual pieces of equipment provide the maximum protection.

11.0 Training and Record Keeping

11.1	Each authorized/affected XXX employee shall be initially trained and annually 	refreshed in the XXX lockout/tagout/tryout procedure and HSEC FRCP #8 	Isolation by a qualified/authorized instructor. This training may take place in 	conjunction with other annual refresher training.

11.2	The training shall include, but not be limited to, FRCP #8 (Isolation), the 	proper PPE for each task, the recognition of hazardous energy sources, the 	types and magnitudes of the energy available in the workplace, and the 	methods and means necessary for energy control.

11.3	 A person shall not be deemed AUTHORIZED until such training has been 	completed and documented.

11.4	Upon completion of training, each employee will fill out an MSHA Form 5000-	23.  The task is to be identified as LOCK/TAG.  The form copies will be 	distributed per instructions.

11.5 	Training documentation will be maintained and remain at site.

11.6  	Training shall be conducted anytime this procedure changes, revised, and 	when 	a change in machinery, equipment, or process presents potential new 	hazards

12.0	Procurement/Replacements

12.1	All equipment shall be purchased with safety and standardization in mind.

12.2	All equipment will be purchased by the using department with changes to stock 	approved by the environmental department and Safety Department.

13.0	Responsibility/Accountability

13.1 	Site manger shall ensure that all requirements specified in this procedure have 	been met and HSEC standards are complied with.

13.2	It is the responsibility of the supervisor to monitor the work to verify 	compliance 	with this procedure.

13.3 	It is the responsibility of the supervisor to ensure that all training as been 	completed in this procedure and in hazard recognition of energy sources and 	the method and means of isolation are met.

13.4	It is the responsibility of the supervisor to ensure that adequate supplies of 	energy isolating devices and lock devices i.e. locks, tags, etc. are readily 	available.

13.5	It is the responsibility of the supervisor to keep copies of their area 	Lockout/Tagout Procedures.

13.6	It is the responsibility of the Safety Department to keep an up-dated copy of the Lockout/Tagout/Tryout Standards.  Copies will be made available for all employees.

13.7 Any changes in this procedure shall require implementation of the change management plan.