|  |  | Originating Department: Safety | Classification: Procedure | E | Q | H&S |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | N | N | Y |
| Date Issued: Revised: |  | Control Number: S-100 |  | Equip Number: N/A |  |  |
| Prepared By: Title: Director of Safety |  | Approved By: Title: Plant Manager | Page 1 of 11 |  |  |  |
| Distribution: | \\Data\Production\Process Related\SOP's Hard Copies: Control Room, Production, Maintenance, Electrical/Instrumentation, Labor, Shipping, Quarry, Lab |  |  |  |  |  |
| Subject: | ENERGY CONTROL PROGRAM (Lock-out/Tag-out) |  |  |  |  |  |

XXX

Revised April 6, 2005

STANDARD OPERATING PROCEDURE

No. S-100

Title:  ENERGY CONTROL PROGRAM (Lock-out/Tag-out)

- POLICY

  - It is the policy of XXXXXX Company that any individual engaging in the maintenance, repairing, cleaning, servicing, or adjusting of prime movers, machinery, or equipment on plant property will abide by the procedures outlined in this document.  These procedures are designed to meet or exceed applicable OSHA and MSHA standards for safe work practices.

  - Lockout is a first means of protection; warning tags only supplement the use of locks.  Tags alone may be used only when the application of a lock is not practically feasible and with approval of the appropriate supervisor.

  - All employees will be protected from injuries caused by unexpected energizing or start up of machines or equipment, or release of stored energy during service, repair, inspection, maintenance, operation, and associated activities.  This policy establishes minimum performance requirements for the control of such potentially hazardous conditions.  This will be accomplished by locking out and tagging out energy isolating devices, and otherwise disabling machines or equipment to prevent unexpected energizing, start up or release of stored energy.

  - Normal production operations are not covered by this policy.  Repairing and/or maintaining equipment during normal production operations are covered by this policy only if:

    - An employee is required to remove or bypass a guard or other safety device; or

    - An employee is required to place any part of his or her body into an area on a machine or piece of equipment where work is actually performed upon the material being processed (point of operation) or where an associated danger zone exists during a machine operating cycle.

  - This policy does not apply to the following:

    - Work on cord and plug connected electric equipment for which exposure to the hazards of unexpected energizing or start up of the equipment is controlled by the unplugging of the equipment from the energy source and by the plug being under the exclusive control of the employee performing maintenance or repair.

    - Hot tap operations involving transmission and distribution systems when they are performed on pressurized pipelines, provided that it has been demonstrated  that;

      - Continuity of service is essential;

      - Shutdown of the system is impractical;

      - Documented procedures are followed, and

      - Special equipment is used which will provide proven effective protection for employees.

- DEFINITIONS

  - Affected Employee:  An employee whose job requires him/her to operate or use a machine or equipment on which maintenance or repair is being performed under this lock-out/tag-out policy, or whose job requires him/her to work in an area in which such maintenance or repair is being performed.

  - Authorized Individual:  A knowledgeable individual to whom the supervisor has given the authority and responsibility to lock or implement a lock-out/tag-out procedure on machines or equipment to perform maintenance or repair.  An authorized individual and an affected employee may be the same person when the affected employee’s duties also include performing maintenance or repair of a machine or equipment that must be locked and tagged out.

  - Knowledgeable Individual:  An individual who is qualified to operate the controls or equipment and is familiar with the effects of operation.

  - “Capable of being locked out”:  An energy isolating device will be considered to be capable of being locked out if it has any of the following;

    - It is designed with a hasp or other attachment or integral part to which, or through which, a lock can be affixed,

    - It has a locking mechanism built into it, or

    - If a lockout can be achieved without the need to dismantle, rebuild, or replace the energy-isolating device or permanently alter its energy control capability.

  - Energy Isolating Device:  A mechanical device that physically prevents the transmission or release of energy, including, but not limited to, the following;  a manually operated electrical circuit breaker, a disconnect switch, a manually operated switch, a slide gate, a slip blind, spectacle flange, a line valve, blocks, and similar devices with a visible indication of the position of the device.  (Push buttons, selector switches, and other control-circuit type devices are not energy isolating devices.)

  - Energy Source:  Any electrical, mechanical, hydraulic, pneumatic, chemical, thermal, gravitational, or other energy source that could cause injury to personnel.

  - Hot Tap:  A procedure used in repair and maintenance activities that involve welding on a piece of equipment (pipelines, vessels or tanks) under pressure, in order to install connections or appurtenances.  It is commonly used to replace or add sections of pipeline without the interruption of service for air, gas, water and steam distribution systems.  Other methods of attachment can also be used.

  - Lock-out Device:  A device that utilizes a lock and key to hold an energy-isolating device in the safe position and prevents a machine or equipment from being energized.

  - Lock-out/Tag-out:  The placement of a lock and tag on the energy isolating device in accordance with an established procedure, indicating that the energy isolating device shall not be operated until removal of the lock/tag in accordance with an established procedure.  (The term “lock-out/tag-out) requires the combination of a lockout device and tag.

  - Maintenance and Repair:  Workplace activities such as constructing, installing, setting up, adjusting, inspecting, modifying, and maintaining machines or equipment.  These activities include but are not limited to lubrication, cleaning or un-jamming of machines or equipment and making adjustments or tool changes, where the employee may be exposed to the unexpected start-up of the equipment or release of hazardous energy.

  - Shall:  The word “shall” always implies a mandatory requirement.

  - Tag-out Device:  A prominent warning device, such as a tag, that can be securely attached to equipment or machinery for the purpose of warning personnel not to operate an energy isolating device and identifying the applier or authority that has control of the procedure.  Example, a come-a-long being used to hold a component in a locked or safe position would be tagged to identify it as an energy control device and not to be removed except by the person who installed it originally.

  - Activation – Energizing:  To set machinery into motion by starting, switching, pushing, moving, or otherwise engaging power sources for such equipment.  To provide a flow of electricity or complete a circuit that is the main power source for the machinery/equipment.

  - Energy Control Procedures:  Use a lock-out/tag-out or other approved devices or equipment to ensure all types of energy are effectively controlled to ensure personal safety.

  - Hazardous Motion:  Motion of equipment under mechanical stress or gravity that may abruptly release and cause injury.  Hazardous motion may result even after power sources are disconnected.  Examples are coiled springs, raised hydraulic equipment, and any sources of potential energy that may cause injury.

  - Prime Mover:  Power driven machinery and equipment.

- RESPONSIBILITIES

  - Safety Department

    - Ensure that the lock-out/tag-out procedures are in compliance with OSHA/MSHA requirements.

    - Maintain a file of equipment, machinery, and operations that require the use of lock-out/tag-out procedures.  The file will include the location, description, power source, and primary hazards of equipment/machinery, a list of the primary operators/maintenance personnel, and a list of lock-out/tag-out equipment that is used and maintained on site.

    - Provides guidance regarding the applicability of the lock-out/tag-out policy.

    - Approves/disapproves exceptions of the lock-out/tag-out policy.

  - Department Heads

    - Ensure that each supervisor adheres to procedures.

  - Supervisors

    - Ensure that each employee and contractor employees engaging in work requiring locking/tagging out of energy sources understands and adheres to these procedures or ensure the contractors procedures are adequate and address all energy sources for the task being performed.

    - Assure that employees have received training in energy control procedures prior to operating the machinery or equipment.

    - Provide and maintain necessary equipment and resources, including accident prevention signs, tags, padlocks, seals and/or other similarly effective equipment for proper energy control.

    - Where applicable, incorporate operation specific lock-out/tag-out procedures into confined space entry or hot work programs for applicable energy control.

    - Notify the safety manager/director of new or revised equipment, machinery, or operations that require the use of lock-out/tag-out devices during servicing, maintenance, or repair.

  - Employees

    - Adhere to specific procedures as outlined in this document for all tasks that require the use of lock-out/tag-out procedures as defined.

    - Maintain lock-out/tag-out supplies in a serviceable condition and readily available for use.

    - Ensure their personal safety lock is marked to identify to whom it belongs.

- SPECIFIC PROCEDURES

  - Preparation for Lock-out/Tag-out

    - Make a survey to locate and identify all isolating devices to be certain which switch(s), valve(s), or other energy isolating devices apply to the equipment to be locked or tagged out.  More than one energy source (electrical, mechanical, stored energy, or others) may be involved.

DANGER!

FAILURE TO PERFORM THE ABOVE STEP MAY RESULT IN DEATH OR SERIOUS PHYSICAL HARM.

  - Sequence of Lock-out or Tag-out System Procedure:

    - Notify affected employees that a lock-out or tag-out system is going to be utilized and the reason therefore.  The authorized employee shall know the type and magnitude of energy that the machine or equipment utilizes and shall understand the hazards thereof.

    - If the machine or equipment is operating, shut it down by the normal stopping procedure (call control room operator, depress stop button, open toggle switch, etc.)

    - Operate the switch, valve, or other energy isolating device(s) so that the equipment is isolated from its energy source(s).  Stored energy (such as that in springs, elevated machine members, rotating flywheels, hydraulic systems, and air, gas, steam, or water pressure, etc.) must be dissipated or restrained by methods such as repositioning, blocking, bleeding down, etc.

      - If there is a possibility of re-accumulation of stored energy to a hazardous level, verification of isolation shall be continued until the maintenance or repair is completed, or until the possibility of such accumulation no longer exists.

DANGER!

FAILURE TO FOLLOW THE NEXT STEP MAY RESULT IN SERIOUS PHYSICAL HARM OR DEATH.

    - Have a qualified electrician turn off the source of electrical energy if the equipment is electrically energized.

    - Lock-out/Tag-out the energy isolating devices with assigned individual lock(s) or tag(s).

    - Verification of Isolation (electrical only):  After ensuring that no personnel can be exposed and as a check on having disconnected the electrical energy source, call the control room operator and have the equipment controls placed in the “Manual” mode and attempt to activate the equipment,  the control room operator must verify that they cannot start the equipment. The control room operator must next place the controls in the “Local” mode of operation.  Maintenance/servicing personnel must attempt to start the equipment using the local push button or other normal operating controls at the field location to make certain the equipment will not operate.  The control room operator must return the controls back to the “Manual” mode of operation and make necessary entries in the lock-out log in the control room. (Verification procedures are located in each group lock-out instructions box in electrical rooms).

CAUTION!

RETURN FIELD OPERATING CONTROL(S) TO NEUTRAL OR OFF POSITION AFTER THE TEST.

    - De-energize, control, or eliminate any remaining energy sources such as air, hydraulic, gravity, or potential motion and install any necessary additional control devices and or lock-out warning tags.

    - The equipment should now be properly locked out or tagged out.

  - Restoring Machines or Equipment to Normal Operations:

    - After the servicing and/or maintenance are complete and equipment is ready for normal productions operations, check the area around the machines or equipment to ensure that no one is exposed.

    - After all tools have been removed from the machine or equipment, guards have been reinstalled and employees are in the clear, remove all lock-out or tag-out devices.  Remove any other energy isolating devices and have a qualified electrician restore electrical energy to the machine or equipment.

  - Procedure Involving More than One Person:

    - In the preceding steps, if more than one individual is required to lock-out or tag-out equipment, each person shall place his/her own personal lock-out/tag-out device on the energy isolating device(s).  When an energy-isolating device cannot accept multiple locks or tags, a multiple lockout or tag-out device (hasp) may be used.  If lock-out is used, a single lock may be used to lockout the machine or equipment with the key being placed in a lockout box or cabinet which allows the use of multiple locks to secure it.  Each employee will then use his/her own lock to secure the box or cabinet.  As each person no longer needs to maintain his or her lock-out protection, that person will remove his/her lock from the box or cabinet.

  - Temporary Removal of Lock-out/Tag-out Devices:

    - In situations where lock-out/tag-out devices must be temporarily removed from the energy isolating device and the machine or equipment energized to test or position the machine, equipment or a component thereof, the following sequence of actions will be followed:

      - Remove non-essential items and ensure that machine or equipment components are operationally intact.

      - Notify affected employees that lock-out/tag-out devices need to be removed and ensure that all employees have been safely positioned or removed from the area.

      - Have employees who applied the lock-out/tag-out devices remove the lock-out/tag-out devices.

      - Energize and proceed with testing or positioning.

      - De-energize all systems and reapply energy control measures in accordance with section 4.2 of these procedures.

  - Maintenance Requiring Undisrupted Energy Supply:

    - Where maintenance, repairing, cleaning, servicing, adjusting, or setting up operations cannot be accomplished with the prime mover or energy source disconnected, such operations may only be performed under the following conditions:

      - The operating station (e.g. external control panel) where the machine may be activated must at all times be under the control of a qualified operator.

      - All participants must be in clear view of the operator or in positive communication with each other.

      - All participants must be beyond the reach of machine elements that may move rapidly and present a hazard.

      - Where machine configuration or size requires that the operator leave the control station to install tools, and where there are machine elements which may move rapidly, if activated, such elements must be separately locked out.

    - During repair procedures where mechanical components are being adjusted or replaced, the machine shall be de-energized or disconnected from its power/energy source.

    - Intermittently operating equipment such as pumps, blowers, fans, compressors, or other machinery will only be allowed when it has been determined that acceptable alternative procedures will afford adequate worker protection and all workers are aware of the special circumstances.  When the need for intermittent operation is no longer necessary, the equipment will immediately be de-energized following established procedures.

- ADDITIONAL REQUIREMENTS

  - Group Lock-out or Tag-out:

    - When a crew, craft, department or other group performs servicing and/or maintenance, they must employ a procedure which protects employees equally as well as a personal lock-out or tag-out device.

    - In the preceding steps, if more than one individual is required to lock out equipment, each shall place a personal lock and tag on the group lockout device when he/she begins work, and shall remove those devices when he/she stops working on the machine or equipment.  The supervisor, with the knowledge of the crew, may lock out equipment for the whole crew.  In such cases, it shall be the responsibility of the supervisor to carry out all steps of the lockout procedure and inform the crew when it is safe to work on the equipment.  Additionally, the supervisor shall place the crew lock key in a lockable box or container kept at the job site (satellite lock box).  Each employee must then place their personal lock on that box/container insuring no one can access the key without their knowledge.  Supervisors shall not remove a crew lock until it has been verified that all individuals are clear.

  - Shift or Personnel Changes:

    - Supervisors shall ensure the continuity of lock-out/tag-out protection during shift or personnel changes.  Each worker shall be responsible for removing his own padlock and tag at the completion of their shift.  If work is to cease until the following day the supervisor shall place his personal padlock and tag or a “SHOP” lock on the equipment and the workers shall remove their padlocks and tags.  (Note: contact information must be available if this procedure is used and someone available to remove the lock in the event of an emergency).  When work resumes the workers shall affix his/her personal lock and tag to the equipment and the supervisor shall remove his lock and tag or shop lock.

  - Outside Personnel (Contractors, etc.)

    - Whenever outside service personnel are to be engaged in activities covered by the scope and application of this policy the Safety Manager and all contractors (including on-site contractors) shall inform each other of their respective lock-out or tag-out procedures.

    - The Safety Manager shall ensure that XXXXXX Company personnel understand and comply with the restrictions and prohibitions of any contractor’s energy control procedures.  Contractors shall ensure that their personnel do likewise for XXXXXXX Company policies as well as other contractor’s policies.

- SPECIAL PROCEDURES (Multiple Energy Sources/Hazards)

  - Equipment Requiring Group Lock-out or Lock Boxes: (Appendix C)

    - Special lock-out-tag-out instructions have been developed for equipment known to contain multiple energy sources or other recognized hazards.  These procedures must be followed exactly.  Each major electrical room contains instructions and lock boxes for this group of equipment.

- TRAINING AND COMMUNICATION

  - Training will be an annual refresher training topic and incorporated into the Part 46 MSHA training plan.

  - The Safety Manager will provide training to ensure that the purpose and function of the energy control program is understood by employees and that the knowledge and skills required for the safe application, usage, and removal of energy controls are required by employees.  The training will include the following:

    - A competent person will train each authorized employee in the recognition of hazardous energy sources, the type and magnitude of the energy available in the workplace, and methods and means necessary for energy isolation and control.

    - Instruct each affected employee in the purpose and use of the energy control procedure.

    - Instruct all other employees whose work operations are or may be in an area where energy control procedures may be utilized, about the procedure, and about the prohibition relating to attempt to restart or reenergize machines or equipment which are locked out or tagged out.

    - Train employees in the limitations of tags when tags are used in lieu of lockout devices.

  - Retraining

    - Retraining will be provided for all authorized and affected employees whenever there is a change in their job assignments, a change in machines, equipment or processes that present a new hazard, or when there is a change in the energy control procedures.

    - Additional retraining shall also be conducted whenever a periodic inspection reveals, or whenever there is reason to believe, that there are deviations from or inadequacies in the employee’s knowledge or use of the energy control procedures.

- RECORD KEEPING

  - Training/Inspection Records:

    - The Safety Department will complete and maintain all training/inspection records in accordance with this policy.

- INSPECTIONS.  (APPENDIX A)

  - The Safety Manager will conduct a periodic inspection of the energy control procedure at least annually to ensure that the procedures and the requirements of this policy are being followed.

  - An authorized employee other than the one(s) utilizing the energy control procedure being inspected shall perform periodic inspections.  The inspections shall be designed to correct any deviations or inadequacies observed.

  - Where lockout is used for energy control, the periodic inspection shall include a review, between the inspector and each authorized employee, of that employee’s responsibilities under the energy control procedure being inspected.

  - The inspector shall certify that the periodic inspections have been performed.  The certification shall identify the machine or equipment on which the energy control procedure was being utilized, the date of the inspection, the employees included in the inspection and the person performing the inspection.

  - Copies of the inspection report shall be sent to the Safety Manager.

- LOCKOUT DEVICE REMOVAL AUTHORIZATION.  (APPENDIX B)

  - In the event a locking device is left on a piece of machinery, switch, etc., attempt to locate the individual(s) or contractor who left it.  If they cannot be located or have left the plant, attempts will be made to recall them to remove their locking device.  A plant employee, if contacted, will be required to return to the plant to remove their locking device, without cost to the company.  If the individual cannot be located, the machinery must be inspected by a supervisor to ensure no one is working on, inside, around, or on top of the machinery.

  - Once a supervisor has determined that it is safe to operate the equipment, he may remove a company lock using the appropriate master key.  Contractor locks may be cut.  All locks removed in this manner will be forwarded to the Safety Manager with a copy of the Lock Removal Authorization form (Appendix B) properly completed and signed by the supervisor authorizing the lock removal.

APPENDIX A

LOCKOUT/TAGOUT INSPECTION FORM

1.	Inspection Date:

- Inspector (Printed Name/Signature):

____________________________________  /  ___________________________________

- Employee(s) Inspected:  (Printed Name  /  Signature):

/

/

/

/

- Machine/equipment on which the energy control procedure was being utilized:

|  |  | YES | NO |
| --- | --- | --- | --- |
| a | Does employee have access to adequate lock out/tag out devices? |  |  |
| b | Has employee tested the effectiveness of his/her lock-out/tag-out devices? |  |  |
| c | Has employee received lock-out/tag-out training in the last year? |  |  |
| d | If this is an outside contractor, has a supervisor informed him/her of the necessity for adhering to these procedures? |  |  |
| e | Have all procedures been followed? |  |  |
| f | Were tag outs legible, durable, weather resistant and clearly displayed? |  |  |

- Comments/Observations:

APPENDIX B

LOCK-OUT DEVICE REMOVAL AUTHORIZATION FORM

Date:

Equipment:

Owner of lock-out device:

Company:

What attempts were made to contact the owner?

Why is it necessary to remove the lock-out device?

Name of Supervisor authorizing removal of lock-out device:

CERTIFICATION / AUTHORIZATION:

I certify that the equipment inspections required by these procedures have been accomplished and the above listed equipment is in a safe condition and no personnel are exposed to operational hazards.  I authorize the removal of the lockout device described above.

Supervisor’s Signature:

APPENDIX C

Equipment containing multiple energy sources with special instructions.

Finnish Mill #1

#1 Finnish Mill Separator

#1 Finish Mill Separator Fan

#1 Finnish Mill Vent Fan

#1 Finnish Mill Discharge Elevator

Mill to Silo Elevator

Finish Mill Motor Bearing Lube System

Finish Mill Bearing Lube System (Fixed and Floating)

J C Steele Feeder

Raw Feed Belt Conveyor (311_BC13)

Vertical Roller Mill

Vertical Mill Reject Elevator (BE23)

Vertical Mill Reducer Lube System

Fly Ash Screw Pump

Vertical Mill Draft Fan

Vertical Mill Air Heater

East Coal Mill

Kiln

Kiln ID Fan (331_FN30)

Clinker Cooler

Conditioning Tower Cooling System

Kiln Feed Elevator (BE10)

Dust Return Elevator (BE76)

Blending Silo Elevator (BE05)

Calciner Burner Primary Air Fan